## Slide 1
Steady-state AC power flow
01
A Python implementation of
the Newton–Raphson method
Project I • EE3810E
[STUDENT NAME] • [STUDENT ID]
[SUPERVISOR NAME] • [DATE]
Notes: Sample English script:
Good morning. This project develops a Python program for steady-state AC power flow using the Newton–Raphson method. I will explain the mathematical model, the custom solver and the evidence supporting the numerical results. The scope is a balanced series-line network.
Điểm cần hiểu:
Nói được mục tiêu; bổ sung tên và GVHD trước khi nộp.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 2
Why calculate power flow?
02
Known network information | Quantities to determine
Demand and scheduled generation | Bus voltage magnitudes and angles
Branch impedances and topology | Sending and receiving powers
Voltage-control setpoints | Slack generation and active losses
Steady state uses fixed phasors for sinusoidal AC operation
Notes: Sample English script:
Demand and scheduled generation do not directly give every voltage or branch flow. Losses depend on current, while current depends on voltage. Power flow resolves this coupled operating point so we can inspect voltages and line power transfers.
Điểm cần hiểu:
Điện áp chưa biết khiến tổn thất chưa biết; đây là bài toán phi tuyến.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 3
Objectives and scope
03
Implemented | Outside the model
Ybus and analytical Jacobian | Line charging and transformer taps
Custom Newton solver and branch flows | Generator reactive and thermal limits
CSV input and shared Streamlit interface | Unbalanced phases, dynamics and OPF
Tests and independent comparison | Large-network performance claims
Notes: Sample English script:
The objective is to build a transparent solver and validate it with reproducible cases. The implementation includes Slack, PV and PQ buses. It uses constant-power demands and series inductive lines. Equipment limits and transient behavior are outside this project.
Điểm cần hiểu:
Phân biệt mô hình đã có và future work; không khẳng định vận hành thực tế khả thi.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 4
The power-flow equations
04
Net injection = generation − demand
I = Ybus V
S = V ⊙ conjugate(I)
x = [δ at non-Slack buses; v at PQ buses]
Three-bus state: [δ₂, δ₃, v₃]ᵀ
Notes: Sample English script:
We define net injection as generation minus demand. Current follows I equals Ybus V. Complex power is voltage times conjugate current. The unknown state contains non-reference angles and PQ voltage magnitudes. The three-bus case therefore has three state variables.
Điểm cần hiểu:
Phải nhớ liên hợp phức và dấu Pg−Pd; góc nội bộ radian.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 5
Bus types and network modeling
05
Bus type | Specified | Solved
Slack | v and δ | P and Q
PV | P and v | δ and Q
PQ | P and Q | v and δ
yᵢⱼ = 1 / (Rᵢⱼ + jXᵢⱼ)
Diagonal: add yᵢⱼ Off-diagonal: subtract yᵢⱼ
Notes: Sample English script:
The reference bus fixes magnitude and angle. A PV bus fixes active injection and magnitude, so its reactive injection is an output. A PQ bus fixes both power injections. Each series admittance contributes positively to two diagonal Ybus entries and negatively to the cross entries.
Điểm cần hiểu:
PV không có phương trình mismatch Q khi vẫn giữ V; một nhánh đóng góp bốn ô Ybus.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 6
Newton–Raphson formulation
06
ΔP = Pspecified − Pcalculated
ΔQ = Qspecified − Qcalculated
Jacobian block | Angle derivative | Magnitude derivative
Active equations | H = ∂P/∂δ | N = ∂P/∂v
Reactive equations | M = ∂Q/∂δ | L = ∂Q/∂v
J Δx = [ΔP; ΔQ] xnew = x + Δx
Notes: Sample English script:
The mismatch is specified power minus calculated power. The Jacobian differentiates calculated injections. Linearization therefore gives J times the correction equals mismatch. We solve this system directly with NumPy, then update only the unknown variables.
Điểm cần hiểu:
Giải thích được dấu của J; H,N,M,L và không dùng inverse.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 7
Iteration and stopping criteria
07
Validate and build Ybus
Initialize voltage state
Evaluate mismatch
Residual below tolerance?
Export solution
Solve J Δx and update
Yes
No
ε = 10⁻¹⁰ pu
30-update limit
Notes: Sample English script:
The algorithm validates the data and builds Ybus once. It calculates mismatch at each state. If the tolerance is reached, it exports the solution. Otherwise, it solves the Jacobian system and repeats. A numerical failure or exhausted update budget produces a diagnostic.
Điểm cần hiểu:
History k=0 là ban đầu; tối đa 30 cập nhật; failure không có nghĩa vô nghiệm.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 8
One shared Python solver
08
CSV and validation
Ybus and power equations
Jacobian and Newton solver
CLI: CSV and plots
Streamlit: tables and downloads
Notes: Sample English script:
The project separates input validation, network construction, power evaluation, derivatives and iteration. Both the command-line script and Streamlit interface call this same core. PYPOWER belongs only to the independent verification script. It is not used to generate the project solution.
Điểm cần hiểu:
Hiểu từng module và dữ liệu qua các bước; không có solver riêng cho UI.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 9
Three-bus test system
09
1 Slack
1.05 pu, 0°
2 PV
P = +0.50 pu, v = 1.02
3 PQ
P = −0.60, Q = −0.25 pu
0.02 + j0.06
0.08 + j0.24
0.06 + j0.18
Series impedances in pu on 100 MVA
Notes: Sample English script:
The supplied case has one Slack bus, one PV generator bus and one PQ load. All quantities use a 100 MVA base. The line model contains only series resistance and reactance. The state vector is delta two, delta three and the third-bus voltage magnitude.
Điểm cần hiểu:
Dữ liệu do đề bài cung cấp, không gán nhãn IEEE.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 10
Three-bus solution
10
Bus | v pu | δ degrees | P net MW | Q net Mvar
1 | 1.050000 | 0.000000 | 12.204693 | 77.807132
2 | 1.020000 | 1.024098 | 50.000000 | -46.193053
3 | 0.984385 | -2.418330 | -60.000000 | -25.000000
Active loss: 2.204693 MW
12.204693 + 50 = 60 + 2.204693 MW
Notes: Sample English script:
The load-bus voltage is about 0.984385 per unit. Bus two has a positive angle and the load bus a negative angle. Total active loss is about 2.204693 megawatts. The Slack generation plus 50 megawatts at bus two equals 60 megawatts demand plus loss. The PV bus absorbs reactive power to hold its specified voltage.
Điểm cần hiểu:
Q âm không nhất thiết sai; chưa kiểm tra giới hạn máy phát.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 11
Convergence and verification
11
Chart: log10 mismatch (pu)
| 0 | 1 | 2 | 3 | 4
log10 residual | -0.20831 | -1.9349 | -4.6147 | -9.9807 | -15.2142
34 tests passed
6 scenarios matched
PYPOWER
Jacobian, balance
and I²R checks
Initial state is update 0; target log10 residual < −10
Notes: Sample English script:
The nominal three-bus case converges in four Newton updates. The chart displays the base-ten logarithm of maximum mismatch, so lower values indicate smaller error. Thirty-four tests pass. The six PYPOWER comparisons agree to near floating-point precision for these small cases.
Điểm cần hiểu:
Đồ thị là log10 residual, không đọc giá trị âm thành mismatch âm.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 12
Five-bus load variation
12
Chart: Active loss (MW)
| 80% | 100% | 120%
Loss MW | 2.6174 | 3.6505 | 5.1437
Load | Min v pu
80% | 0.980615
100% | 0.968039
120% | 0.954938
Synthetic system, 100 MVA base, fixed generator schedules
Notes: Sample English script:
The second network is synthetic. Demand scales to eighty, one hundred and one hundred twenty percent while generation schedules and voltage setpoints stay fixed. The minimum voltage falls and active losses rise for these cases. This experiment does not establish a stability limit.
Điểm cần hiểu:
Nói được synthetic và tải PV tăng khiến Pnet giảm.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 13
Limitations and next steps
13
Current limitation | Consequence / next step
Unlimited generator reactive power | Add and verify PV-to-PQ switching
Series-only branches | Add charging and transformer models
Dense, undamped Newton | Investigate sparse matrices and step control
Small educational cases | Validate larger benchmark networks
Browser upload/download and local installation need review
Notes: Sample English script:
A mathematical power-flow solution does not certify real operating feasibility. This model excludes reactive capability, voltage bounds and thermal ratings. The solver is dense and undamped. My first proposed extension is reactive-limit handling with PV-to-PQ switching, followed by additional branch models.
Điểm cần hiểu:
Các mở rộng chưa làm; không dùng kết quả để nhận xét ổn định động.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 14
Conclusions
14
Objective | Evidence
Custom numerical implementation | Explicit Ybus, Jacobian and Newton updates
Reproducible results | CSV inputs, results JSON and residual histories
Verification | 34 tests and six independent comparisons
Explainable method | Worked iteration and module walkthrough
Verified computations within a clearly stated model
Notes: Sample English script:
The project connects circuit equations to a transparent Python implementation. Both networks and all six load scenarios are reproducible. The verification evidence supports the algorithm within its stated assumptions. The remaining academic work is supervisor review, personal information completion and demonstrating understanding of the derivation and code.
Điểm cần hiểu:
Không nhận bộ nháp kỹ thuật là đã được GVHD duyệt; sinh viên phải tự chạy và hiểu.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html

## Slide 15
Thank you
15
Questions and discussion
Model assumptions
Newton update
Verification evidence
Notes: Sample English script:
Thank you for listening. I welcome questions about the model assumptions, the Jacobian, numerical verification or the code. I can also demonstrate one Newton update and explain the limitations of the current implementation.
Điểm cần hiểu:
Chuẩn bị demo mạng 3 bus và file first_iteration.json; trả lời trung thực phần đã hiểu.
Sources: Project results/results.json and original implementation. Technical formulation: https://matpower.app/manual/matpower/ACPowerFlow.html