HANOI UNIVERSITY OF SCIENCE AND TECHNOLOGY
SCHOOL OF ELECTRICAL AND ELECTRONIC ENGINEERING
DEPARTMENT OF POWER SYSTEMS

PROJECT I REPORT (COURSE EE3810E)

AC POWER FLOW ANALYSIS USING NEWTON--RAPHSON METHOD: MATHEMATICAL FORMULATION, STEP-BY-STEP NUMERICAL VERIFICATION, AND SOFTWARE CROSS-VALIDATION

| Author / Student: | La Huy Gia Huy |
| --- | --- |
| Student ID: | 202412885 |
| Cohort / Class: | EE - E18 (Elite Engineering Program) |
| Academic Program: | Power Systems and Renewable Energy - 02 |
| Academic Supervisor: | Dr. Nguyen Hoang Viet |
| Department & School: | Power Systems Department, SEEE, HUST |

HANOI, ACADEMIC YEAR 2026--2027

# PROJECT ASSIGNMENT SHEET

1. Student Name: La Huy Gia Huy 	 Student ID: 202412885
2. Cohort / Degree Program: EE - E18, Power Systems and Renewable Energy - 02 (SEEE - HUST)
3. Project Title: AC Power Flow Analysis using Newton--Raphson Method: Mathematical Formulation, Step-by-Step Numerical Verification, and Software Cross-Validation
4. Supervisor: Dr. Nguyen Hoang Viet (Department of Power Systems)
5. Objectives: Establish polar AC power flow equations, derive analytical 4-block Jacobian matrix, perform transparent Iteration 1 hand calculation on 3-bus network, validate against developed numerical solver to IEEE-754 precision, and evaluate 4 operational grid scenarios.

# EXECUTIVE SUMMARY

Steady-state AC power flow analysis is the foundational mathematical technique underpinning power systems engineering, serving as the prerequisite for operational security dispatch, expansion planning, voltage stability assessment, and contingency analysis. This project establishes a comprehensive, white-box, three-tier engineering methodology: (1) rigorous analytical formulation of polar power equations and closed-form Jacobian derivatives (H, N, M, L); (2) transparent step-by-step manual numerical benchmark on a 3-bus transmission system for Iteration 1; and (3) multi-tier software cross-validation to IEEE-754 double precision alongside 4 operational scenario assessments (load scaling, PV voltage regulation, shunt capacitive compensation, and N-1 transmission line outage contingencies).

# Chapter 1: Introduction

## 1.1 Fundamental Role of AC Power Flow

Load flow calculations resolve steady-state nodal voltages (U, delta) to calculate active/reactive branch flows, equipment thermal duties, and system losses.

## 1.2 Scope and Objectives

Formulate white-box polar NR algorithm, execute manual Iteration 1 benchmark, validate against developed numerical solver, and analyze operational regimes.

## 1.3 Three-Tier Methodology

Tier 1: Analytical continuous mathematics; Tier 2: Step-by-step hand calculation; Tier 3: Machine-precision software cross-validation.

# Chapter 2: Power System Modeling & Network Topology

## 2.1 Per-Unit System

Base scaling laws on S_base = 100 MVA eliminate transformer turns ratios and unify single-phase and three-phase power equations.

## 2.2 Line and Transformer Pi-Models

Nominal pi-equivalent circuits model series impedance z = r + jx and half-line charging susceptance b0 = B/2.

## 2.3 Bus Classification

Slack Bus (U1=1.05 pu, delta1=0 deg), PV Bus (P_G2=0.5 pu, U2=1.02 pu), and PQ Bus (P_D3=0.6 pu, Q_D3=0.25 pu).

## 2.4 Static ZIP Load Modeling

Polynomial load representation combining constant impedance, constant current, and constant power components.

## 2.5 Nodal Admittance Matrix Assembly

Assembled via KCL: Y_ii = sum(y_ij) + y_i0; Y_ij = -y_ij.

# Chapter 3: Mathematical Formulation & Newton--Raphson Solver

## 3.1 Polar AC Power Flow Equations

Calculated powers in rectangular admittance form: P_i = sum(U_i U_j (G_ij cos(delta_ij) + B_ij sin(delta_ij))); Q_i = sum(U_i U_j (G_ij sin(delta_ij) - B_ij cos(delta_ij))).

## 3.2 Multivariable Taylor Linearization

Mismatch system J * dx = f, where f = [Delta P, Delta Q]^T and dx = [Delta delta, Delta U]^T.

## 3.3 Analytical Closed-Form Jacobian

Complete 8 formulas: H_ij, H_ii = -Q_i - B_ii U_i^2; N_ij, N_ii = P_i/U_i + G_ii U_i; M_ij, M_ii = P_i - G_ii U_i^2; L_ij, L_ii = Q_i/U_i - B_ii U_i.

## 3.4 Stopping Criteria and Unit Discipline

Infinite-norm mismatch max(|Delta P|, |Delta Q|) <= 1e-10 pu. Delta delta in radians converted to degrees for reporting.

## 3.5 Post-Convergence Physical Flow Calculations

Branch flows S_ij, line losses Delta S_ij = S_ij + S_ji, and global energy balance audit: sum(P_G) - sum(P_D) - Delta P_loss = 0.

# Chapter 4: Numerical Verification & Operational Scenarios

## 4.1 Step-by-Step Hand Benchmark (m = 0 -> 1)

P2_calc = -0.119000 pu, P3_calc = -0.095833 pu, Q3_calc = -0.287500 pu; Delta P2 = +0.619000 pu, Delta P3 = -0.504167 pu, Delta Q3 = +0.037500 pu. Initial Jacobian J(0) inverted to yield Delta delta2 = +1.043303 deg, Delta delta3 = -2.359247 deg, Delta U3 = -0.013885 pu.

## 4.2 Software Cross-Validation

Direct 1:1 comparison confirms absolute discrepancy < 1e-16 pu (exact IEEE-754 precision). Solver converges in 4 iterations with global loss = 2.204693 MW and zero power balance residual.

## 4.3 Scenario 1: Load Scaling

Load scaled 80% -> 120%: U3 drops from 0.994686 to 0.973711 pu, losses rise from 1.739606 to 2.834110 MW (+62.9%).

## 4.4 Scenario 2: PV Voltage Tuning

V2 tuned 0.98 -> 1.05 pu: Q_G2 shifts from -118.13 to +11.96 Mvar, elevating U3 from 0.960154 to 1.002482 pu and reducing losses by 70%.

## 4.5 Scenario 3: Shunt Capacitor Compensation

Q_C = 20 Mvar at Bus 3 elevates U3 to 1.005518 pu and reduces transmission losses by 12.02%.

## 4.6 Scenario 4: N-1 Contingencies

Line 2-3 outage shifts meshed loop to radial feed, depressing U3 to 0.924591 pu (<0.95 grid limit) and surging losses by +139.4%.

# Chapter 5: Conclusion & Engineering Insights

## 5.1 Achievements Summary

Theoretical derivation, exact manual verification, machine-precision software cross-validation, and operational insights successfully delivered.

## 5.2 Core Engineering Insights

Demonstrated quadratic convergence rate and physical decoupling (P-delta and Q-U) in high-voltage grids.

## 5.3 Future Research Directions

Fast Decoupled Power Flow (FDPF), Sparse LU matrix factorization for large IEEE grids, and Optimal Power Flow (OPF).

## Key Numerical Verification Tables

Table: Iteration 1 Cross-Validation (Hand Calculation vs. Developed Solver)

| Variable | Hand Calc | Developed Solver | Abs Discrepancy | Status |
| --- | --- | --- | --- | --- |
| P2_calc (pu) | -0.119000 | -0.119000 | 0.000000 | Exact |
| P3_calc (pu) | -0.095833 | -0.095833 | < 1e-16 | Exact |
| Q3_calc (pu) | -0.287500 | -0.287500 | 0.000000 | Exact |
| Delta P2 (pu) | +0.619000 | +0.619000 | 0.000000 | Exact |
| Delta P3 (pu) | -0.504167 | -0.504167 | < 1e-16 | Exact |
| Delta Q3 (pu) | +0.037500 | +0.037500 | 0.000000 | Exact |
| Delta delta2 (deg) | +1.043303 | +1.043303 | < 1e-15 | Exact |
| Delta delta3 (deg) | -2.359247 | -2.359247 | < 1e-15 | Exact |
| U3 (Iteration 1) | 0.986115 | 0.986115 | < 1e-16 | Exact |

Table: Full Convergence Trajectory (Tolerance = 1e-10 pu)

| Iter (m) | U3 (pu) | delta2 (deg) | delta3 (deg) | Max Mismatch (pu) | Status |
| --- | --- | --- | --- | --- | --- |
| 0 | 1.000000 | 0.000000 | 0.000000 | 6.1900e-01 | Flat Start |
| 1 | 0.986115 | +1.043303 | -2.359247 | 1.1618e-02 | Iterating |
| 2 | 0.984386 | +1.024102 | -2.418296 | 2.4284e-05 | Iterating |
| 3 | 0.984385 | +1.024098 | -2.418330 | 1.0454e-10 | Iterating |
| 4 | 0.984385 | +1.024098 | -2.418330 | 6.1062e-16 | Converged |

Table: Post-Contingency N-1 Line Outage Screening

| Outaged Line | Status | Vmin (pu) | Worst Bus | P_loss (MW) | Iters | Assessment |
| --- | --- | --- | --- | --- | --- | --- |
| None (Base) | Converged | 0.984385 | Bus 3 | 2.204693 | 4 | Compliant |
| Line 1-2 | Converged | 0.983620 | Bus 3 | 2.022847 | 4 | Compliant |
| Line 1-3 | Converged | 0.927755 | Bus 3 | 3.396328 | 4 | Voltage Violation |
| Line 2-3 | Converged | 0.924591 | Bus 3 | 5.277141 | 4 | Severe Violation |